## Slide 1: Healthcare Power System Installations and Case Studies
Nov 3rd, 2022 1:00 Eastern / 10:00 Pacific (1 PDH issued by Cummins Inc.)
PowerHour webinar series for consulting engineers Experts you trust.
Excellence you count on.

## Slide 2: Welcome!
Cummins PowerHour webinar series is designed to help our engineer partners to…
Keep up to date on products, technology, and codes and standards development
Interact with Cummins experts and gain access to ongoing technical support
Participate at your convenience, live or on-demand
Earn Professional Development Hours (PDH)
Technical tips:
Audio is available through teleconference or Zoom application.
Attendees are in “listen only” mode throughout the event.
Use the Zoom Q&A Panel to submit questions, comments, and feedback throughout the event. Time is allotted at the end of the PowerHour to address Q&A.
If the audio connection is lost, disconnected or experiences intermittent connectivity issues, please check your audio connection through the "Join Audio" or "Audio Connectivity" button at the bottom left of the Zoom application.
Report technical issues using the Zoom Q&A Panel.
Notes: Welcome to the Cummins PowerHour webinar series, the program designed for our engineering partners like you!
The program offers concise technical presentations on topics pertaining to on-site power systems design and specification. The program aims to keep you updated on products, technology and codes and standards development, the topics most relevant to the jobs and projects you are working on.
You can earn 1 Professional Development Hour issued by Cummins upon your completion of the webinar.
This webinar will be recorded and archived. If you miss a webinar, or want to visit our archive of content, please visit our on-demand webinar center and replay any topic.
We have muted the conference line to ensure a quality sound environment during the presentation.
If you do experience any challenges with the audio broadcast during today’s PowerHour, please navigate to the “Join Audio” button on the bottom left of your Zoom application to ensure your device is connected and test your device if needed.

## Slide 3: Asking a Question:
Q&A Button:
For technical questions on today’s topic
Ask at anytime
Not all questions may get answered but we’ll do our best!
Chat Button:
For general PowerHour or Zoom questions
Notes: You are encouraged to ask your questions throughout today’s PowerHour. Our expert panelists will do their best to address questions through text answers during the presentation, or verbally in the Q&A session at the end of the PowerHour.
Also, at times, our speaker may pose questions to you! If we ask you a multiple choice question, we will prompt a poll that will appear through Zoom. For open-ended questions, however, we encourage you to click that “chat” button to engage with our speakers and panelists. We love seeing your engagement to our questions!

## Slide 4: Meet your panelists
Cummins instructors:
Chad Hale
Technical Marketing Specialist
Cummins Inc.
Chris Scott​
Senior Sales Application Engineer​
Cummins Inc.

## Slide 5: Disclaimer
The views and opinions expressed in this course shall not be considered the official position of any regulatory organization and shall not be considered to be, nor be relied upon as, a Formal Interpretation.
Participants are encouraged to refer to the entire text of all referenced documents. In addition, when it doubt, reach out to the Authority Having Jurisdiction.

## Slide 6: Course Objectives
Healthcare Power System Installations and Case Studies:
As the number of healthcare facilities in North America continue to grow, so does the need for emergency power supply systems to back up those facilities. Further, the wide variety of healthcare facilities can make for a seemingly dauting task of requirements management. This presentation will cover those key installation requirements and common codes and standards while also discussing several unique healthcare application installations.
After completing this course, participants will be able to:
Describe the common codes and standards associated with healthcare applications
Identify key design attributes along with the service and maintenance requirements for a healthcare power system.
Recognize the challenges impacting healthcare power systems and find solutions via case studies.

## Slide 7
?
What are some of the key codes and standards associated with an emergency power supply system within a health care application?

## Slide 8: Key Considerations Codes and Standards – NFPA 110
Requirements covering the performance of emergency and standby power systems providing an alternate source of electrical power to loads in buildings and facilities in the event that the primary power source fails.

## Slide 9: Key Considerations Codes and Standards – NFPA 110
Requirements covering the performance of emergency and standby power systems providing an alternate source of electrical power to loads in buildings and facilities in the event that the primary power source fails
Covers installation, maintenance, operation, and testing requirements as they pertain to the performance of the emergency power supply system (EPSS).

## Slide 10: Key Considerations Codes and Standards – NFPA 110
Requirements covering the performance of emergency and standby power systems providing an alternate source of electrical power to loads in buildings and facilities in the event that the primary power source fails.
Covers installation, maintenance, operation, and testing requirements as they pertain to the performance of the emergency power supply system (EPSS)
Intent of standard is to achieve maximum system reliability

## Slide 11: Key Considerations Codes and Standards – NFPA 110
Requirements covering the performance of emergency and standby power systems providing an alternate source of electrical power to loads in buildings and facilities in the event that the primary power source fails.
Covers installation, maintenance, operation, and testing requirements as they pertain to the performance of the emergency power supply system (EPSS)
Intent of standard is to achieve maximum system reliability
NFPA 110 Time to Readiness
White Paper
PowerHour Recording
Related Content

## Slide 12: Key Considerations Codes and Standards – NFPA 110 – Type 10
Type:
  Maximum time, in seconds, that the EPSS will permit the load terminals of the transfer switch to be without acceptable electrical power (NFPA 4.3) Time generator has to operate after a power failure.
The emergency power supply system provides acceptable power to the load side of the transfer switch within 10 seconds after an outage
This 10 second includes all intentional and unintentional delays associated with transfer.

## Slide 13: Key Considerations Codes and Standards – NFPA 99
Requirements covering the performance of emergency and standby power systems providing an alternate source of electrical power to loads in buildings and facilities in the event that the primary power source fails.
Covers installation, maintenance, operation, and testing requirements as they pertain to the performance of the emergency power supply system (EPSS)
Intent of standard is to achieve maximum system reliability
Notes: When stating NFPA 99 put the name of the code “health care facilities code” NFPA is standard for EPSS …. OSHPD hard wire network check with Brian P.

## Slide 14: Key Considerations Codes and Standards – NFPA 99
Requirements covering the performance of emergency and standby power systems providing an alternate source of electrical power to loads in buildings and facilities in the event that the primary power source fails.
Covers installation, maintenance, operation, and testing requirements as they pertain to the performance of the emergency power supply system (EPSS)
Intent of standard is to achieve maximum system reliability
Divides the essential electrical system into three branches: life safety, critical, and equipment
Notes: When stating NFPA 99 put the name of the code “health care facilities code” NFPA is standard for EPSS …. OSHPD hard wire network check with Brian P.

## Slide 15: Key Considerations Codes and Standards – NEC 700.3
Emergency system shall include a permanent means to connect to a temporary source of power
Notes: More clarity on tap boxes.. No mention of the connection box. Check in with NEC 2017 changes slide deck. Look into different single line diagrams and removing current pic, typical schematic

## Slide 16: Key Considerations Codes and Standards – NEC 700.3
Emergency system shall include a permanent means to connect to a temporary source of power
Tap Boxes
Provide a solution for connecting a temporary source of power while a generator is down
Notes: More clarity on tap boxes.. No mention of the connection box. Check in with NEC 2017 changes slide deck. Look into different single line diagrams and removing current pic, typical schematic

## Slide 17: Key Considerations Joint Commission - Environment of Care Standard
Tested 12 times a year at intervals no less than 20 days and no more than 40 days

## Slide 18: Key Considerations Joint Commission - Environment of Care Standard
Tested 12 times a year at intervals no less than 20 days and no more than 40 days
Test each emergency generator for at least 30 continuous minutes and test dates must be documented

## Slide 19: Key Considerations Joint Commission - Environment of Care Standard
Tested 12 times a year at intervals no less than 20 days and no more than 40 days
Test each emergency generator for at least 30 continuous minutes and test dates must be documented
The emergency generator tests are conducted with a dynamic load that is at least 30% of the nameplate rating of the generator or meets the manufacturer’s recommended prime movers’ exhaust gas temperature
Joint Commission
jointcommission.org
Related Content
Recommendation: For additional guidance, see NFPA 110, Standard for Emergency & Standby Power Systems.

## Slide 20: Key Considerations Canadian Standards Association
CSA C282:19
Emergency electrical power supply for buildings
CSA-Z32
Electrical safety and essential electrical systems in healthcare facilities

## Slide 21
?
What are some of the common maintenance and testing requirements of an emergency power supply system within a health care application?

## Slide 22: Key Considerations Testing – Monthly NFPA 110
8.4.2 Generator sets in service shall be exercised at least once monthly, for a minimum of 30 minutes, using one of the following methods:
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 23: Key Considerations Testing – Monthly NFPA 110
8.4.2 Generator sets in service shall be exercised at least once monthly, for a minimum of 30 minutes, using one of the following methods:
  Loading that maintains the minimum exhaust gas temperatures as recommended by the manufacturer
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 24: Key Considerations Testing – Monthly NFPA 110
8.4.2 Generator sets in service shall be exercised at least once monthly, for a minimum of 30 minutes, using one of the following methods:
  Loading that maintains the minimum exhaust gas temperatures as recommended by the manufacturer
  Under operating temperature conditions and at not less than 30 percent of the EPS standby nameplate kW rating
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 25: Key Considerations Testing – Monthly NFPA 110
8.4.2 Generator sets in service shall be exercised at least once monthly, for a minimum of 30 minutes, using one of the following methods:
  Loading that maintains the minimum exhaust gas temperatures as recommended by the manufacturer
  Under operating temperature conditions and at not less than 30 percent of the EPS standby nameplate kW rating
Recommendation Test emergency generator sets at least monthly for at least 30 minutes with a load bank at no less than 30% of the generator set rating.
Specifying Testing for Reliable Power Systems
PowerHour
Related Content
Notes: Mention NFPA 110
EGTs specified by the manuf.. In the AEB
Bullet 1 being more specific to after treatment (cali.. 100 percent HC recommend DPF sometimes up to 80 percent to keep it hot)

## Slide 26: Key Considerations Testing – 36 Months NFPA 110
8.4.9 Level 1 EPSS shall be tested at least once within every 36 months.
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 27: Key Considerations Testing – 36 Months NFPA 110
8.4.9 Level 1 EPSS shall be tested at least once within every 36 months.
8.4.9.1 Level 1 EPSS shall be tested continuously for the duration of its assigned class.
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 28: Key Considerations Testing – 36 Months NFPA 110
8.4.9 Level 1 EPSS shall be tested at least once within every 36 months.
8.4.9.1 Level 1 EPSS shall be tested continuously for the duration of its assigned class.
8.4.9.2 Where the assigned class is greater than 4 hours, it shall be permitted to terminate the test after 4 continuous hours.
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 29: Key Considerations Testing – 36 Months NFPA 110
8.4.9 Level 1 EPSS shall be tested at least once within every 36 months.
8.4.9.1 Level 1 EPSS shall be tested continuously for the duration of its assigned class.
8.4.9.2 Where the assigned class is greater than 4 hours, it shall be permitted to terminate the test after 4 continuous hours.
8.4.9.5 The minimum load for this test shall be as specified in 8.4.9.5.1, 8.4.9.5.2, or 8.4.9.5.3.
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 30: Key Considerations Testing – 36 Months NFPA 110
8.4.9 Level 1 EPSS shall be tested at least once within every 36 months.
8.4.9.1 Level 1 EPSS shall be tested continuously for the duration of its assigned class.
8.4.9.2 Where the assigned class is greater than 4 hours, it shall be permitted to terminate the test after 4 continuous hours.
8.4.9.5 The minimum load for this test shall be as specified in 8.4.9.5.1, 8.4.9.5.2, or 8.4.9.5.3.
8.4.9.6 The test required in 8.4.9 shall be permitted to be combined with one of the monthly tests required by 8.4.2 and one of the annual tests required by 8.4.2.3 as a single test.
Recommendation Specify a permanent load bank to the system to allow for proper loading during weekly testing
NFPA 110 Time to Readiness
White Paper
PowerHour Recording
Related Content
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 31: Key Considerations Maintenance – Manufacturer Requirements
Routine Maintenance and Operational Testing
8.1.1 The routine maintenance and operational testing program shall be based on all of the following:
  (1) Manufacturer’s recommendations
  (2) Instruction manuals
  (3) Minimum requirements of this chapter
  (4) The authority having jurisdiction
Notes: Look into fuel maintenance so… quality…. look for mark and mikes presentation for slides

## Slide 32: Key Considerations Maintenance – Legal Compliance
Routine Maintenance and Operational Testing
8.1.1 The routine maintenance and operational testing program shall be based on all of the following:
  (1) Manufacturer’s recommendations
  (2) Instruction manuals
  (3) Minimum requirements of this chapter
  (4) The authority having jurisdiction
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 33: Key Considerations Maintenance – AHJ Requirements
Routine Maintenance and Operational Testing
8.1.1 The routine maintenance and operational testing program shall be based on all of the following:
  (1) Manufacturer’s recommendations
  (2) Instruction manuals
  (3) Minimum requirements of this chapter
  (4) The authority having jurisdiction
EPA Emissions Regulations
PowerHour
White Paper
Related Content
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 34: Key Considerations Maintenance – Fuel Testing
8.3.7 A fuel quality test shall be performed at least annually using appropriate ASTM standards or the manufacturer’s recommendations.
Notes: Look into fuel maintenance so… quality…. look for mark and mikes presentation for slides

## Slide 35: Key Considerations NFPA 110 Compliance Reporting
Generators serve as reliable emergency supply in a multitude of mission critical applications
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 36: Key Considerations NFPA 110 Compliance Reporting
Generators serve as reliable emergency supply in a multitude of mission critical applications
An established record of maintenance and operational testing is needed for emergency power supply systems
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 37: Key Considerations NFPA 110 Compliance Reporting
Generators serve as reliable emergency supply in a multitude of mission critical applications
An established record of maintenance and operational testing is needed for emergency power supply systems
Compliance agencies refer to NFPA 110 guidelines
  Joint Commission on Accreditation of Healthcare Organizations
  Centers for Medicare and Medicaid
  Internal Audits conducted by several mission critical organizations
  Local Authority Having Jurisdiction
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 38: Key Considerations NFPA 110 Compliance Reporting – Remote Monitoring
One-Click Reporting
  Provides a quick access to pre-formatted, pre-approved NFPA 110 template in Cummins PCC branding
  Make provisions for the customer to make a final “Pass or Fail” assessment, without having to print hard copies of the report
  Provides a single report per site avoiding need to download multiple asset-by-asset report
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 39: Key Considerations NFPA 110 Compliance Reporting – Remote Monitoring
One-Click Reporting
  Provides a quick access to pre-formatted, pre-approved NFPA 110 template in Cummins PCC branding
  Make provisions for the customer to make a final “Pass or Fail” assessment, without having to print hard copies of the report
  Provides a single report per site avoiding need to download multiple asset-by-asset report
Leverage regular Generator Start/Stops for Testing
  With manual reporting – the only alternative facilities had was to schedule a test and conduct ‘meter reading’ at the equipment
  Ability to use any actual outages or generator operations for test reporting purposes
Notes: Detection of failure: does not necessarily mean loss of power, ATS are susceptible to damage (voltage dip if outside of the range, so it could be considered failure of the normal source).
ATS waits: now that the transfer switch has detected the failure, it waits a short period of time.
ATS sends signal to genset: these two steps could take about a second.
Generator set initiates engine start sequence: engine starts to ramp up, the ramping up itself may take the majority of the time in this 10 second window, this can take anywhere between 4 to 8.5 seconds.
Genset reach “ready to load”: it is ready to accept the load (90% rated voltage and frequency)
ATS does its job: transfer load from normal to neural position so nothing is connected to loads
Transfer time delay: transfer from neutral to emergency position

## Slide 40: Key Considerations NFPA 110 Compliance Reporting – Remote Monitoring
Data graph summarizing the test results
Data table summarizing the test results
Notes: Left is the test itself.. Right is the run report .. Hard to read whats on the right side switch to bullet points instead of the word bubbles and enlarge pics. Report tab is not available for everyone

## Slide 41: Key Considerations NFPA 110 Compliance Reporting – Remote Monitoring
Summary table, with editable field for test results
Notes: Left is the test itself.. Right is the run report .. Hard to read whats on the right side switch to bullet points instead of the word bubbles and enlarge pics. Report tab is not available for everyone

## Slide 42: Key Considerations NFPA 110 Compliance Reporting – Remote Monitoring
New Reports Tab on PCC
Notes: Left is the test itself.. Right is the run report .. Hard to read whats on the right side switch to bullet points instead of the word bubbles and enlarge pics. Report tab is not available for everyone

## Slide 43: Key Considerations NFPA 110 Compliance Reporting – Remote Monitoring
Based on generator runtime duration, Facility manager can either create report or discard event
Notes: Left is the test itself.. Right is the run report .. Hard to read whats on the right side switch to bullet points instead of the word bubbles and enlarge pics. Report tab is not available for everyone

## Slide 44: Key Considerations NFPA 110 Compliance Reporting – Remote Monitoring
Last 45 days stored
Notes: Left is the test itself.. Right is the run report .. Hard to read whats on the right side switch to bullet points instead of the word bubbles and enlarge pics. Report tab is not available for everyone

## Slide 45: Healthcare Power Systems Applications and Capability

## Slide 46: Healthcare Installation Review
Application: Standby and Hurricane Relief
Segment: Medical Center (763 Licensed Beds)
Location: Louisiana, US
Key Acceptance Criteria
NFPA 110 Type 10 Starting for Life Safety Loads
Extended Run Time (>24 Hours)
Operational Flexibility
Case Study
Related Content

## Slide 47: Healthcare Installation Review
Application: Life Safety Standby with Demand Response
Segment: Hospital
Location: Salem, OR
Key Acceptance Criteria
Complete system one source and one manufacturer
Operational Flexibility
System Design
Stringent acoustical and footprint requirements
Case Study
Related Content

## Slide 48: Healthcare Installation Review
Application: Life Safety Standby
Segment: Hospital (133 Licensed Medical Beds)
Location: Calgary, Alberta, Canada
Key Acceptance Criteria
Complete system one source and one manufacturer
(3) 2000kW, Medium Voltage, Paralleled
Remote Location
Case Study
Related Content

## Slide 49: Course Summary
Healthcare Power System Installations and Case Studies:
Describe the common codes and standards associated with healthcare applications
Identify key design attributes along with the service and maintenance requirements for a healthcare power system.
Recognize the challenges impacting healthcare power systems and find solutions via case studies.

## Slide 50: Additional Resources
Cummins White Papers​
10-Second Time to Readiness
EPA Emission Regulations: What They Mean for Diesel Powered Generator Systems
Maintenance is One Key to Diesel Generator Set Reliability
Cummins PowerHour On-Demand Webinars​
NFPA 110 Type 10 Requirements for Emergency Power Systems
Emissions and Air Permitting Requirements for Standby Generator Sets
Considerations for Specifying Generator Set Fuel Sources
The Role of a System Level Control in a Power System
Specifying Generator Set Testing for Reliable Power Systems
Application Manuals
T-030 – Liquid Cooled Generator Sets

## Slide 51: Q&A
Please type your questions, comments and feedback in the Zoom Q&A window.
Copy of the presentation, and link to the recording will be provided in a follow up email within a 1-2 business days.
Please complete the brief survey upon exiting the webinar!
Chad Hale
Technical Marketing Specialist
Cummins Inc.
Chris Scott​
Senior Sales Application Engineer​
Cummins Inc.

## Slide 52: Following This Event…
First Email (ASAP)​
1 Professional Development Hour (PDH) Certificate
Please engage with our exit survey!
Second Email (3-5 Business Days)
Video Recording
Copy of slide deck
Power Suite
Power Suite is where to find past PowerHours, Application Manuals, Sizing Tools, Data Sheets, and more!
Please contact us if you have any questions related to the PowerHour webinar (PowerGenChannel@cummins.com)
Notes: In closing, watch out for two follow-up emails from us. The first will be shortly after this event with your certificate for one professional development hour. Within a few business days, keep an eye out for a second email with links to this video recording and a copy of the slide deck for your later reference.
After the close of this event, you will see a brief survey. We ask that you please take the time to complete that survey, your feedback is greatly appreciated and helps us to improve this program for future events and participants.
As always, considering visiting Cummins PowerSuite at powersuite.cummins.com for past webinar recording, technical information and sizing and specification development tools.

## Slide 53: More From Cummins!
Cummins White Papers​
Click here to subscribe!
Cummins On-Demand Webinars​
Click here for our full webinar library!
Click here to subscribe!
Brightest Bulbs Podcast
Click here to hear about the latest innovations in energy and power!
New Transfer Switch Product
Your Strongest Link to Reliable Power is Now Here! Learn more about the PowerCommand® X-Series Transfer Switch here!
Upcoming Live PowerHour:
04/28/2022 – Transfer Switches Features and Functions
Notes: Cummins is your partner in professional continuing education through PowerHours, TechStream, Lunch and Learns and other continuing education programs. When you get the copy of this slide deck, click any of these links to sign up for subscriptions, podcasts, and our back-catalog of PowerHours.
Watch out for our next Cummins PowerHour, Transfer Switches: Features and Functions.

## Slide 54
Notes: Lastly, our network of Application Engineers can bring technical presentations and expert advice to you and are backed up directly with our factory team of product and code specialist ensuring the best professional network at your disposal. If you don’t know who your local Application Engineer is, you can reference this map!
These Cummins application engineers are happy to help you by providing technical information, designing and specifying assistance in order to comply with local, regional, state and national regulations.
Thank you for attending this Cummins PowerHour, we hope to see you next month for another exciting topic.