## Slide 1: NFPA® 110 FOR EMERGENCY POWER SYSTEMS DESIGN REQUIREMENTS
December 15th 2:00 Eastern / 10:00 Pacific (1 PDH issued by Cummins Inc.)
PowerHour webinar series for consulting engineers Experts you trust.
Excellence you count on.
Notes: A warm welcome and thank you for attending this session.
I'm ( Peter Larson ) , and I'll be covering the basics of NFPA standard 110.
------------------------------------------------------------------------------------------------

## Slide 2: Welcome!
Cummins PowerHour webinar series is designed to help our engineer partners to…
Keep up to date on products, technology, and codes and standards development
Interact with Cummins experts and gain access to ongoing technical support
Participate at your convenience, live or on-demand
Earn Professional Development Hours (PDH)
Technical tips:
Audio is available through teleconference or Zoom application.
Attendees are in “listen only” mode throughout the event.
Use the Zoom Q&A Panel to submit questions, comments, and feedback throughout the event. Time is allotted at the end of the PowerHour to address Q&A.
If the audio connection is lost, disconnected or experiences intermittent connectivity issues, please check your audio connection through the "Join Audio" or "Audio Connectivity" button at the bottom left of the Zoom application.
Report technical issues using the Zoom Q&A Panel.
Notes: Welcome to the Cummins PowerHour webinar series, the program designed for our engineering partners like you!
The program offers concise technical presentations on topics pertaining to on-site power systems design and specification. The program aims to keep you updated on products, technology and codes and standards development, the topics most relevant to the jobs and projects you are working on.
You can earn 1 Professional Development Hour issued by Cummins upon your completion of the webinar.
This webinar will be recorded and archived. If you miss a webinar, or want to visit our archive of content, please visit our on-demand webinar center and replay any topic.
We have muted the conference line to ensure a quality sound environment during the presentation.
If you do experience any challenges with the audio broadcast during today’s PowerHour, please navigate to the “Join Audio” button on the bottom left of your Zoom application to ensure your device is connected and test your device if needed.

## Slide 3: Asking a Question:
Q&A Button:
For technical questions on today’s topic
Ask at anytime
Not all questions may get answered but we’ll do our best!
Chat Button:
For general PowerHour or Zoom questions
Notes: You are encouraged to ask your questions throughout today’s PowerHour. Our expert panelists will do their best to address questions through text answers during the presentation, or verbally in the Q&A session at the end of the PowerHour.
Also, at times, our speaker may pose questions to you! If we ask you a multiple choice question, we will prompt a poll that will appear through Zoom. For open-ended questions, however, we encourage you to click that “chat” button to engage with our speakers and panelists. We love seeing your engagement to our questions!

## Slide 4: Meet your panelists
Cummins instructors
Cummins facilitator
Chad Hale
Technical Marketing Cummins Inc.
Nibal Kiwan Sales Application Engineering Leader – Africa/Middle East Cummins Inc..
Peter Larson Global SAE Technical Advisor Cummins Inc..

## Slide 5: Disclaimer
The views and opinions expressed in this course shall not be considered the official position of any regulatory organization and shall not be considered to be, nor be relied upon as, a Formal Interpretation.
Participants are encouraged to refer to the entire text of all referenced documents. In addition, when it doubt, reach out to the Authority Having Jurisdiction.

## Slide 6: Course Objectives
NFPA110 - Emergency Power Systems
This course will provide an overview of NFPA 110, focusing on the implications of Type 10 systems as they relate to the emergency power supply system (EPSS) and the emergency power source (EPS). Participants will take a look into the 10-second start requirement and the impact this has on the generator set while also discussing features that support NFPA 110 requirements such as cooling systems, coolant heaters, and fuel systems.
After completing this course, participants will be able to:
Recognize NFPA 110 classifications of emergency and standby power systems
Identify key aspects and intent of NFPA 110 that impact equipment selection and design of generator set emergency power systems.
Describe various strategies for ensuring generator set and system performance as they relate to NFPA 110 Type 10 guidelines.
Notes: Course Objectives:
It’s easy to add a line in a project specification for NFPA 110, but what does that drive? Actually, quite a lot.
We have limited time in this session, so we will focus on NFPA 110 Type 10 , which revolves around the 10-second requirement.
- After this course, you'll be able to recognize NFPA 110 classifications with regards to what they actually mean.
- How those classifications impact equipment selection.
And
Describe strategies to ensure your system meets the standard.
--------------------------------------------------------------------------------------

## Slide 7: NFPA 110 Introduction Overview
Standard for Emergency and Standby Power Systems (NFPA 1.1)
Requirements covering the performance of emergency and standby power systems providing an alternate source of electrical power to loads in buildings and facilities in the event that the primary power source fails. (NFPA 1.1)
Covers installation, maintenance, operation, and testing requirements as they pertain to the performance of the emergency power supply system (EPSS). (NFPA 1.2).
This standard is also intended to provide guidance for inspectors, designers, installers, manufacturers, and users of EPSS and to serve as a vehicle of communication between parties involved. It is not intended as a design manual. (NFPA 1.2.2).
Intent of standard is to achieve maximum system reliability.
Notes: NFPA 110 Introduction:
NFPA is an independent organization, they publishes around 300 codes and standards.
The 110 standard deals with requirements of Emergency and Standby power SYSTEMS.
------------------------------------------------------------------------------------------------------------------

## Slide 8: NFPA 110 Introduction Definitions
NFPA® and National Fire Protection Association® are registered trademarks of the National Fire Protection Association, Quincy, MA. All rights reserved.
NFPA – National Fire Protection Association
EPS – Emergency Power Source: Source of electrical power (standby generator) independent from primary source of power.
EPSS – Emergency Power Supply System: Backup power system which includes EPS, transfer switches, load terminals and equipment to provide alternative source of power.
AHJ – Authority Having Jurisdiction: Agencies responsible for enforcing code compliance, it varies per region.
Notes: NFPA 110 Definitions:
Here some basic definitions and acronyms we'll see in this presentation.
N F P A National Fire Protection Association
E P S refers to the standby generator (Emergency Power Source)
E P S S refers to the EPS, Transfer switch, load terminals, and other equipment to make the SYSTEM
A H J (Authority Having Jurisdiction) has a big role in the installations.
----------------------------------------------------------------------------------------------

## Slide 9: NFPA 110 Introduction Definitions
E P S
Emergency Power Source
Notes: Definitions:
This slide shows the E P S , Emergency Power Source ( in this case it’s Standby generators )
------------------------------------------------------------------------------------------------------------

## Slide 10: NFPA 110 Introduction Definitions
E P S S
Emergency Power Supply System
Notes: Definitions:
And now you see the additional components that make up a E P S S ( Emergency Power Supply System -- the complete system )
One of the biggest pitfalls of project specifications and commissioning, can be traced back to a mis-interpretation of terms.
Component requirements can be very different than System requirements.
---------------------------------------------------------------------------------------------

## Slide 11: Classification of E P S S
E P S S are classified by Class, Type, Level :
  Class:
  Minimum time, in hours, for which the EPSS is designed to operate at its rated load without being refueled or recharged. (NFPA 4.2)
  Type:
  Maximum time, in seconds, that the EPSS will permit the load terminals of the transfer switch to be without acceptable electrical power. (NFPA 4.3)
  Level:
  This standard recognizes two levels of equipment installation, performance and maintenance. (NFPA 4.4).
Notes: Classification of a E P S S
The three terms :
1.) CLASS ( minimum time to keep the genset running – fuel )
2.) TYPE ( maximum time to re-establish electrical power)
3.) LEVEL ( levels of equipment installation, performance, and maintenance of the E P S S )
Let’s go into more detail ( click for the next slides )
----------------------------------------------------------

## Slide 12: Classification of EPSS
  Class:
  Minimum time, in hours, for which the EPSS is designed to operate at its rated load without being refueled or recharged. (NFPA 4.2)
EPSS are classified by Class, Type, Level:
Notes: C L A S S
This is the NFPA table 4.1 (a), and it shows:
Minimum time ( in hours) for which the E P S S is designed to operate at its rated load without being refueled or recharged.
Keep in mind that this is the MINIMUM time
Notice the time is expressed in HOURs
-----------------------------------------------------------

## Slide 13: Classification of EPSS
EPSS are classified by Class, Type, Level:
  Type:
  Maximum time, in seconds, that the EPSS will permit the load terminals of the transfer switch to be without acceptable electrical power. (NFPA 4.3)
Notes: T Y PE
This is the NFPA table 4.1 (b), and it shows:
Maximum time, (In seconds), that the EPSS will allow the load terminals of the transfer switch to be without acceptable electrical power.
Keep in mind that this is the MAXIMUM time
Notice that the time is expressed in SECONDs
-----------------------------------------------------------

## Slide 14: Classification of EPSS
EPSS are classified by Class, Type, Level :
  Level:
  This standard recognizes two levels of equipment installation, performance and maintenance. (NFPA 4.4).
  Level 1: Systems shall be installed where failure of the equipment to perform could result in loss of human life or serious injuries. (NFPA 4.4.1)
  Level 2: Systems shall be installed where failure of the EPSS to perform is less critical to human life and safety. (NFPA 4.4.4)
  NFPA 110 does not state which applications are Level 1 or Level 2, the levels are determined by other codes and the AHJ .
Notes: LEVEL
NFPA 110 has two levels of E P S S ( Remember … LEVEL meaning Equipment installation, Performance, and Maintenance ).
LEVEL 1, is the most strict, and focuses on loss of human life or serious injury.
Level 1 is associated to NEC Article 700, life safety loads
LEVEL 2, is anything less than Level 1.
Level 2 is associated with NEC Article 701, legally required loads.
Typically the AHJ will have a large input into what LEVEL is required.
All parties need to work together to define the system, and how NFPA 110 requirements will be met.
----------------------------------------------------------------------------------------------------------------------

## Slide 15: Concept Check
?
NFPA 110 defines “TYPE” as …
Minimum time, in hours, for which the EPSS is designed to operate at its rated load without being refueled or recharged.
Maximum time, in seconds, that the EPSS will permit the load terminals of the transfer switch to be without acceptable power.
Redundancy level, number of emergency power sources, that the EPSS will include.
Prototype testing requirements for emergency power source vendors.
Notes: CONCEPT CHECK
We talked about " TYPE ", Select the best answer …. ( answer is B )
---------------------------------------------------------------------------------

## Slide 16: Concept Check

NFPA 110 defines “TYPE” as …
Minimum time, in hours, for which the EPSS is designed to operate at its rated load without being refueled or recharged.
Maximum time, in seconds, that the EPSS will permit the load terminals of the transfer switch to be without acceptable power.
Redundancy level, number of emergency power sources, that the EPSS will include.
Prototype testing requirements for emergency power source vendors.
Notes: CONCEPT CHECK , ANSWER
Answer B is correct, ( TYPE deals with the time the emergency load terminals will be without power )
The other terms we covered were: Class ( fuel run time) and Level ( severity )
--------------------------------------------------------------------------------------------------------

## Slide 17: Single Generator Set EPSS
Reference: NFPA 110 Edition 2019, ANNEX B.1 (a) Diagrams of Typical Systems
Notes: Single Genset E P S S
We’re looking at a typical single generator set E P S S (System).
In this design, we have one Utility (normal source), one Genset ( emergency source )
The 3 Transfer Switches determine the selection of where the Emergency Loads receive their electrical energy.
* if asked … cover this topology in detail, not everyone will understand this graphic symbols *
-------------------------------------------------------------------------------

## Slide 18
?
What happens after the normal source fails in an emergency power system?
Notes: QUESTION
What do you think happens after the normal source ( UTILITY ) fails ?
We will cover the Sequence of Events in the next slides ...
-------------------------------------------

## Slide 19: Utility Outage – Single Generator Set System Sequence of Events
ATS control detects failure of normal source
ATS programmed time delay before next step
ATS control sends start signal to generator set control
Generator set control initiates engine start sequence
Generator set engine starts
Generator set reaches “Ready to Load”
ATS transitions from normal to neutral position
ATS transitions from neutral to emergency position
Notes: This slide shows the complete Sequence of Events for a simple design
We will cover the individual steps in the next slides:
----------------------------------------------------------------

## Slide 20: Utility Outage – Single Generator Set System Sequence of Events
ATS control detects failure of normal source
ATS programmed time delay before next step
ATS control sends start signal to generator set control
Generator set control initiates engine start sequence
Generator set engine starts
Generator set reaches “Ready to Load”
ATS transitions from normal to neutral position
ATS transitions from neutral to emergency position
0.5 – 1.0 Seconds based on application
Notes: SEQUENCE OF EVENTS
Step 1 ) Detection of failure:
Loss of utility voltage. This does not necessarily mean a total outage, the ATS control could respond to severe voltage dip.
Step 2 ) ATS waits:
A short period of time to determine if the Utility voltage returns
Step 3 ) ATS sends signal to genset:
If the Utility voltage does not return, the ATS control will send a start command to the genset.
Theses three steps take about ½ to 1 second
---------------------------------------------------------------

## Slide 21: Utility Outage – Single Generator Set System Sequence of Events
ATS control detects failure of normal source
ATS programmed time delay before next step
ATS control sends start signal to generator set control
Generator set control initiates engine start sequence
Generator set engine starts
Generator set reaches “Ready to Load”
ATS transitions from normal to neutral position
ATS transitions from neutral to emergency position
0.5 – 1.0 Seconds based on application
4.0 – 8.0 Seconds based on generator set configuration
Notes: SEQUENCE OF EVENTS
Step 4 ) Genset receives the start command:
The genset control receive the start command from the ATS
Step 5 ) Engine crank / start:
The genset control issues commands to get the engine cranking and fueling for rated speed, voltage regulator is turned on to produce the rated voltage ( excitation )
Step 6 ) Genset is ready for load:
At 90% rated voltage and 90% rated frequency, the genset control issues a "Ready-to-Load" signal
These three steps can add 4 to 8 seconds
----------------------------------------------------------

## Slide 22: Utility Outage – Single Generator Set System Sequence of Events
ATS control detects failure of normal source
ATS programmed time delay before next step
ATS control sends start signal to generator set control
Generator set control initiates engine start sequence
Generator set engine starts
Generator set reaches “Ready to Load”
ATS transitions from normal to neutral position
ATS transitions from neutral to emergency position
0.5 – 1.0 Seconds based on application
4.0 – 8.0 Seconds based on generator set configuration
0.5 – 1.0 Seconds based on transfer switch and application
Notes: SEQUENCY OF EVENTS
Step 7 ) ATS changes switch position:
The ATS switch move its contacts to the Neutral position (no power source is connected to loads).
Step 8 ) ATS changes switch position:
The ATS switch move its contracts to the Emergency position, this is the Finish Line according to the standard
Theses last two steps can take ½ to 1 second.
---------------------------------------------------------------------------------------------------

## Slide 23: Utility Outage – Time Delay on Start
6.2.5 Time Delay on Starting of EPS.
  A time-delay device shall be provided to delay starting of the EPS. The timer shall prevent nuisance starting of the EPS and possible subsequent load transfer in event of harmless momentary power dips and interruptions of the primary source.
A.6.2.5
  For most applications, a nominal delay of 1 second is adequate. The time delay should be short enough so that the generator can start and be on line within the time specified for the type classification.
Notes: QUESTION ?
What happens if you are right on the edge of meeting the type 10 requirements ?
- One solution is to adjust the start command time delay.
NFPA 110 mandates a "delay on start". “A time delay device shall be provided, to delay the starting of EPS, the timer shall prevent nuisance starting of the EPS”
This delay intent is to prevent the genset from being commanded to start from a minor voltage disturbance.
The standard doesn't say is how long that time delay should be, all it says is that it “shall be required"
In the appendix there is a note explaining this requirement.
A normal delay of 1 second is adequate ... so that's a good starting point.
Most transfer switch manufacturers ship their transfer switches with a 1 second delay.
I want to reinforce that 1 second is not firm, it can be adjusted to a shorter period.
We sometimes come across installations where the owners would rather be more sensitive to power fluctuations and start the gensets even when the 10 seconds can be met. This is a good information to remember.
--------------------------------------------------------------------

## Slide 24
Paralleled Generator Sets EPSS
Reference: NFPA 110 Edition 2019, ANNEX B.1 (b) Diagrams of Typical Systems
Notes: Multiple Gensets in a E P S S
Let’s do this exercise again, with 3 paralleled gensets.
----------------------------------------------------------------

## Slide 25
ATS control detects failure of normal source
ATS programmed time before next step
ATS control sends start signal to generator set control
Generator set control initiates engine start sequence
Generator set engine starts
Generator set reaches “Ready to Load”
Generator set paralleling controls begin “first start arbitration”
  Generator set that “wins” first start arbitration proceeds to next step
  All other generator sets must synchronize before proceeding to the next step
Generator set paralleling circuit breaker closes
ATS transitions from normal to neutral position
ATS transfer time delay
ATS transitions from neutral to emergency position
0.5 – 1.0 Seconds based on application
Utility Outage - Multiple Generator Set System Sequence of Events
Notes: SEQUENCE OF EVENTS - Steps 1, 2, 3 ….... Same as the single genset example
Step 1 ) Detection of failure:
Loss of utility voltage. Does not necessarily mean a total outage, the ATS control could respond to severe voltage dip.
Step 2 ) ATS waits:
A short period of time to determine if the Utility voltage returns
Step 3 ) ATS sends signal to genset:
If the Utility voltage does not return, the ATS control will send a start command to the gensets.
These three steps take about ½ to 1 second

## Slide 26
ATS control detects failure of normal source
ATS programmed time before next step
ATS control sends start signal to generator set control
Generator set control initiates engine start sequence
Generator set engine starts
Generator set reaches “Ready to Load”
Generator set paralleling controls begin “first start arbitration”
  Generator set that “wins” first start arbitration proceeds to next step
  All other generator sets must synchronize before proceeding to the next step
Generator set paralleling circuit breaker closes
ATS transitions from normal to neutral position
ATS transitions from neutral to emergency position
0.5 – 1.0 Seconds based on application
4.0 – 8.0 Seconds based on generator set configuration
Utility Outage - Multiple Generator Set System Sequence of Events
Notes: SEQUENCE OF EVENTS – Steps 4, 5, 6 …... Same as the single genset example
Step 4 ) Genset controls receives the start command:
The genset control receive the start command from the ATS
Step 5 ) Engine crank / start:
The genset controls issues commands to get to engine / alternator started and running (cranking signal, fueling, excitation)
Step 6 ) Genset is ready for load:
At the 90% rated voltage and 90% rate frequency, the genset is "Ready-to-Load"
These three steps can add 4 to 8 seconds

## Slide 27
ATS control detects failure of normal source
ATS programmed time before next step
ATS control sends start signal to generator set control
Generator set control initiates engine start sequence
Generator set engine starts
Generator set reaches “Ready to Load”
Generator set paralleling controls begin “first start arbitration”
  Generator set that “wins” first start arbitration proceeds to next step
  All other generator sets must synchronize before proceeding to the next step
Generator set paralleling circuit breaker closes
ATS transitions from normal to neutral position
ATS transitions from neutral to emergency position
0.5 – 1.0 Seconds based on application
4.0 – 8.5 Seconds based on generator set configuration
0.5 – 1.0 Second for first generator set
0.5 – 1.0 Second for each additional generator set
Utility Outage - Multiple Generator Set System Sequence of Events
Notes: SEQUENCE OF EVENTS – Step 7, 8 ….... are Different from the single genset example
STEP 7 ) First genset "Ready-to-Load"
This is where things are different than a single genset.
Note, in this application, each genset control is configured for Island Paralleling Application.
When the first genset reaches Ready-to-Load, it will close its circuit breaker to the dead bus.
This genset becomes the Master and now triggers the other gensets to undergo step 8.
STEP 8 ) Synchronize and Arbitration
The remaining gensets are prohibited from closing to the bus until they synchronize, and then they arbitrate the order of which genset is next to close its circuit breaker.
Step 8 can add an additional 0.5 – 1 second for each genset.

## Slide 28
ATS control detects failure of normal source
ATS programmed time before next step
ATS control sends start signal to generator set control
Generator set control initiates engine start sequence
Generator set engine starts
Generator set reaches “Ready to Load”
Generator set paralleling controls begin “first start arbitration”
  Generator set that “wins” first start arbitration proceeds to next step
  All other generator sets must synchronize before proceeding to the next step
Generator set paralleling circuit breaker closes
ATS transitions from normal to neutral position
ATS transitions from neutral to emergency position
0.5 – 1.0 Seconds based on application
4.0 – 8.5 Seconds based on generator set configuration
0.5 – 1.5 Seconds based on transfer switch and application
0.5 – 1.0 Second for first generator set
0.5 – 1.0 Second for each additional generator set
Utility Outage - Multiple Generator Set System Sequence of Events
Notes: SEQUENCE OF EVENTS …. Same as the single genset example
Step 9 ) ATS changes switch position:
The ATS switch move its contracts to the Neutral position (no power source is connected to loads).
Step 10 ) ATS changes switch position:
The ATS switch moves its contracts to the Emergency position, this is the Finish Line according to the standard
Note: We recommend some caution when specifying Paralleling gensets for applications that require NFPA 110 Type 10.
- The other gensets add more time.
- The smallest kW genset that could be connected to the bus, must be sized to meet the Type 10 loads.
Theses last two steps can take ½ to 1 seconds.

## Slide 29: E P S - Subsystems
Batteries, Starting & Charging Systems.
Fuel Storage and Delivery Systems
Temperature Maintenance and Cooling Systems
Notes: ( E P S ) GENSET SUBSYSTEMS
NFPA 110 drives design requirements for the genset manufacturer and the site installation.
You will need to know about these subsystems:
- Electrical …Batteries, Battery charger, Engine starting motors
- Fuel Storage and Delivery system
- Genset Cooling systems

## Slide 30: E P S - Subsystems Batteries, Starting and Charging Systems
5.6.4.1 Starting Systems
  Starting shall be accomplished using either an electric or a stored energy starting system.
5.6.4.3 Number of Batteries.
  Each prime mover shall be provided with both of the following:
  Storage battery units as specified in Table 5.6.4.2
5.6.4.4 Size of Batteries.
  The battery unit shall have the capacity to maintain the cranking speed recommended by the prime mover manufacturer through two complete periods of cranking limiter time-outs as specified in Table 5.6.4.2, item (d).
Notes: GENSET SUBSYSTEMS - batteries and starting system
We'll begin with the starting system
NFPA 110 states that “starting shall be accomplished using either an electric or a stored energy system”.
Electric starting system is the most common.
"Stored energy starters" usually refers to compressed air starters, not as common, but are still allowed.
Note: the air supply must be large enough to complete three-cycle cranking time.
Batteries
The next part calls for the correct number & size of batteries to meet the required cranking cycles.
Looking at this table, you can see a total of 75 seconds.
That’s generally interpreted as 3 cycles of 15 seconds of engine cranking followed by 15 seconds rest.
The key here is that most genset manufacturers have verified the starting system performance.
Reach out the genset manufacturers with questions.

## Slide 31: Generator Set Subsystems Batteries, Starting and Charging Systems
5.6.4.6 Automatic Battery Charger
  In addition to the prime mover- (engine-) driven charger required in 5.6.3.6.1, a battery charger(s), as required in Table 5.6.4.2, shall be supplied for maintaining a charge on both the starting and control battery unit.
Notes: GENSET SUBSYSTEMS - battery charging
NFPA 110 calls for an automatic battery charger to be included in the design.
The battery charger keeps the starting and control batteries fully charged when the genset is not running.
Assure the battery charger is compatible with the battery Chemistry.
--------------------------------------------------------------------------------------------------

## Slide 32: Generator Set Subsystems Batteries, Starting and Charging Systems
5.6.4.7
  All chargers shall include the following characteristics, which are to be accomplished without manual intervention (i.e., manual switch or manual tap changing):
  At its rated voltage, the charger shall be capable of delivering energy into a fully discharged battery unit without damaging the battery.
  The charger shall be capable of returning the fully discharged battery to 100 percent of its ampere-hour rating within the time specified in Table 5.6.4.2, item (f).
  As specified in Table 5.6.4.2, item (e), meters with an accuracy within 5 percent of range shall be furnished.
  The charger shall be permanently marked with the following:
    Allowable range of battery unit capacity
    Nominal output current and voltage
    Sufficient battery-type data to allow replacement batteries to be obtained
  The battery charger output and performance shall be compatible with the batteries furnished.
Notes: GENSET SUBSYSTEMS - battery charger requirements
For Level 1 systems, the battery charger shall be sized so it completely recharges the battery from 0 to 100% in 24 hours.
Genset manufacturers will typically recommend the correct type and size battery charger.
-------------------------------------------------------------------------------------------------------

## Slide 33: Generator Set Subsystems Fuel Storage and Delivery Systems
7.9.1.2
  Fuel system design shall provide for a supply of clean fuel to the prime mover.
7.9.1.3
  Tanks shall be sized so that the fuel is consumed within the storage life, or provisions shall be made to remediate fuel that is stale or contaminated or to replace stale or contaminated fuel with clean fuel.
8.3.7
  A fuel quality test shall be performed at least annually using appropriate ASTM standards or the manufacturer’s recommendation.
Notes: GENSET SUBSYSTEMS – Fuel
The next subsystem is the fuel tanks.
Remember size or quantity is correlated to CLASS (runtime) .
From the maintenance perspective: Tanks shall also be sized so that fuel is consumed within the storage life of 12-16 months, that's in the ideal conditions.
Questions to ask …How many hours does a generator set run a year ? Is that genset run time going to burn all the fuel and then refilled with fresh fuel ?
If the fuel is not consumed, then it should be regularly sampled, and if needed, cleaned through a fuel polishing process.
------------------------------------------------------------------------------------------------------------------------------

## Slide 34: Generator Set Subsystems Temperature Maintenance and Cooling Systems
5.3.1
  The EPS shall be heated as necessary to maintain the water jacket and battery temperature determined by the EPS manufacturer for cold start and load acceptance for the type of EPSS.
Notes: GENSET SUBSYSTEMS – Engine Temperature
The next subsystem requirement covers the engine coolant heater.
To meet the start time requirements, the engine block temperature must be maintained at a temperature specified by the E P S manufacturer.
Genset manufacturers will size the correct coolant heater for various ambient temperatures.
Many specification call out a coolant heater wattage, we discourage this verbiage.
-------------------------------------------------------------------------------------------------------

## Slide 35: Generator Set Subsystems Temperature Maintenance and Cooling Systems
5.6.7.3
  Cooling systems shall prevent overheating of prime movers under conditions of highest anticipated ambient temperature at the installed elevation (above sea level) when fully loaded.
  Standard ratings: 40°C (104°F) / 50°C (122 °F)
Notes: GENSET SUBSYSTEMS – Cooling
The cooling subsystem requirement is cited in NFPA 110.
In summary:
NFPA requires the cooling system to be sized appropriately for the installation; site elevation and highest ambient temperature.
Typically, we recommend that the genset manufacturers design and test the cooling system’s capability.
Note: remote cooled application can become more of a concern since this design isn't factory tested.
-----------------------------------------------------------------------------------------------------

## Slide 36: Generator Set Subsystems Temperature Maintenance and Cooling Systems
Notes: GENSET SUBSYSTEMS – Cooling
Just a note worth mentioning … please understand how genset manufactures specifies cooling performance.
Here we have an indoor application … Alternator is to the left, Engine in the center, Radiator on the right.
------------------------------------------------------------------------------------------------------------------------------

## Slide 37: Generator Set Subsystems Temperature Maintenance and Cooling Systems
Depending on room design, ∆T can be 3-10 °C (5-18 °F)
Air Temperature
Ambient
Air-on-core
Notes: GENSET SUBSYSTEMS – Cooling
This photo shows the air flow across the genset, air movement is Left to Right.
Depending on the room design, the temperature reaching the radiator & charged air cooler can rise 3 - 10 C degrees.
The additional heat comes from the alternator, engine, and exhaust components.
A caution on cooling system marketing … know how the cooling system is marketed:
40 C Ambient ( the design includes allowance for the additional heat degrees )
or
40 C Air-on-Core ( no allowance for the additional heat degrees ) … to start the Ambient temperature must be lower than 40C
---------------------------------------------------------------------------------------------------

## Slide 38: Concept Check
?
Which of the following EPS sub-systems may impact the EPSS’s ability to meet NFPA 110 Type 10 requirements?
Fuel system design and quality of fuel
Engine coolant heater
Starting batteries and starters
All of the above
Notes: CONCEPT CHECK
What subsystems can have an impact on the TYPE 10 time ? ( Answer is D )
------------------------------------------------------------------------------------------------------

## Slide 39: Concept Check

Which of the following EPS sub-systems may impact the EPSS’s ability to meet NFPA 110 Type 10 requirements?
Fuel system design and quality of fuel
Engine coolant heater
Starting batteries and starters
All of the above
Notes: CONCEPT CHECK ANSWER
The answer is D, all of the items have an impact.
----------------------------------------------------------

## Slide 40: Course Summary
NFPA 110 Type 10 Requirements for Emergency Power Systems
Recognize NFPA 110 classifications of emergency and standby power systems.
Identify key aspects and intent of NFPA 110 that impact equipment selection and design of generator set emergency power systems.
Describe various strategies for ensuring generator set and system performance as they relate to NFPA 110 Type 10 guidelines.
Specify:
Type requirement as it pertains to the power system.
The smallest generator set on the generator set paralleling bus shall have sufficient capacity to support all emergency loads.
Site testing and maintenance practices that maintain system reliability such as fuel quality testing and battery check-ups.
NFPA 110 prototype testing compliance and documentation of prototype testing.
Avoid specifying:
NFPA 110 “certification” for generator sets or other components.
Notes: COURSE SUMMARY
We reached the end of the course, and learned …. KEY WORDS, STRATEGIES, and PERFORMANCE REQUIREMENTS.
Additional Key points to remember:
- NFPA 110 is a standard, not a certification. Genset manufacture design for installation compliance.
- Mixing components / subsystems from different manufactures may affect the TYPE rating.
- When using a genset paralleling bus, assure the smallest kW genset can supply the emergency loads.
- Specify prototype testing and documentation.
With that ..... we'll move to QUESTIONS and ANSWERS
----------------------------------------------------------------------

## Slide 41: Additional Resources
Cummins White Papers​
10-Second Time to Readiness
EPA Emission Regulations: What They Mean for Diesel Powered Generator Systems
Maintenance is One Key to Diesel Generator Set Reliability
Cummins PowerHour On-Demand Webinars​
NFPA 110 Type 10 Requirements for Emergency Power Systems
Emissions and Air Permitting Requirements for Standby Generator Sets
Considerations for Specifying Generator Set Fuel Sources
The Role of a System Level Control in a Power System
Specifying Generator Set Testing for Reliable Power Systems
Application Manuals
T-030 – Liquid Cooled Generator Sets

## Slide 42: Q&A
Please type your questions, comments and feedback in the Zoom Q&A window.
Copy of the presentation, and link to the recording will be provided in a follow up email within a 1-2 business days.
Please complete the brief survey upon exiting the webinar!
Chad Hale
Technical Marketing Cummins Inc.
Nibal Kiwan Sales Application Engineering Leader – Africa/Middle East Cummins Inc..
Peter Larson Global SAE Technical Advisor Cummins Inc..

## Slide 43: Following This Event…
First Email (ASAP)​
1 Professional Development Hour (PDH) Certificate
Please engage with our exit survey!
Second Email (3-5 Business Days)
Video Recording
Copy of slide deck
Power Suite
Power Suite is where to find past PowerHours, Application Manuals, Sizing Tools, Data Sheets, and more!
Please contact us if you have any questions related to the PowerHour webinar (PowerGenChannel@cummins.com)
Notes: In closing, watch out for two follow-up emails from us. The first will be shortly after this event with your certificate for one professional development hour. Within a few business days, keep an eye out for a second email with links to this video recording and a copy of the slide deck for your later reference.
After the close of this event, you will see a brief survey. We ask that you please take the time to complete that survey, your feedback is greatly appreciated and helps us to improve this program for future events and participants.
As always, considering visiting Cummins PowerSuite at powersuite.cummins.com for past webinar recording, technical information and sizing and specification development tools.

## Slide 44: More From Cummins!
Cummins White Papers​
Click here to subscribe!
Cummins On-Demand Webinars​
Click here for our full webinar library!
Click here to subscribe!
Brightest Bulbs Podcast
Click here to hear about the latest innovations in energy and power!
New Transfer Switch Product
Your Strongest Link to Reliable Power is Now Here! Learn more about the PowerCommand® X-Series Transfer Switch here!
Upcoming Live PowerHour:
04/28/2022 – Transfer Switches Features and Functions
Notes: Cummins is your partner in professional continuing education through PowerHours, TechStream, Lunch and Learns and other continuing education programs. When you get the copy of this slide deck, click any of these links to sign up for subscriptions, podcasts, and our back-catalog of PowerHours.
Watch out for our next Cummins PowerHour, Transfer Switches: Features and Functions.

## Slide 45
Notes: Lastly, our network of Application Engineers can bring technical presentations and expert advice to you and are backed up directly with our factory team of product and code specialist ensuring the best professional network at your disposal. If you don’t know who your local Application Engineer is, you can reference this map!
These Cummins application engineers are happy to help you by providing technical information, designing and specifying assistance in order to comply with local, regional, state and national regulations.
Thank you for attending this Cummins PowerHour, we hope to see you next month for another exciting topic.